# BELOW GRADE WATERPROOFING GUIDELINES

For use on exterior walls and on mud slabs to prevent moisture penetration and or liquid escape from interior tanks.

1.		Modified bitumen (pitch) incorporating Dupont's Ethylene Interpolymer (EIP)

2.		Self-adhering with a rubber modified asphalt adhesive backing

3.		Membrane shall be no less than 75 mil

4.		Membrane shall inhibit root growth/penetration

5.		Properties:

Color							Black

Tensile strength				1500 psi

Elongation					70%

Tear strength				270 ppi

Water absorption			Less than 0.1%

Chemical resistance		Good to excellent

6.		Membrane described:	Hyload WS self-adhesive membrane with welded seams

7.		Suggested Manufacturer:

Hyload, Inc

5020 Panther Pkwy.; Seville, OH 44273

Toll Free Tel: 800-457-4056

Tel: 330-769-3546

Web: www.hyload.com

8.		Asphaltic underground membranes are discouraged on UK projects.