VAV CONTROL				DGP Requirement	Local Indication

Supply Fan S/S					DO

Supply Fan Status				DI

SF Inlet Vane Pos				AO

SF Duct Static					AI

O.A. Damper Pos				AO

Freeze Stat Alm					DI

High Static Alm/Rst				DI

Filter Alm							DI

TEMPERATURE CONTROL

Supp Air Temp					AI

Ret Air Temp					AI

Mixed Air Temp					AI

Valve Pos						AO

2-7# HTG

8-13#CLG

Zone Space Temp				AI

HW Pump 1A S/S				DO

HW Pump 1A Status			DI

HW Pump 1B S/S				DO

HW Pump 1B Status			DI

RETURN FAN

Return RF S/S					DO

Return RF Status				DI

Space Stat						AI

RRF Inlet Vane Pos			AO

RF Damper Pos					AO

OPTIONAL POINTS

SF Static Pressure				AI

60 Min Ext Ser Sw.				DI

SOFTWARE CONTROL

Fan discharge air temperature by control of CW Valve, HW Valve and damper position.

Duct static pressure by control of SF inlet vane, OA damper pos and MA damper pos.

Return fan tracking to maintain design space static.

Sequence of operation.

NOTE:

The VAV pumps and reheat piping and valving shall be separate and independent of the unit ventilators and fan coil unit hot water zoning to allow the heating system to be automatically turned off in most of the building during summer months.