- Prefilters shall consist of a pleated media, media support grid, and enclosing frame.   The filters shall be labeled by Underwriters Laboratories as Class 2.

- The media shall be a non-woven cotton fabric and shall have a minimum efficiency (ASHRAE test standard 52 - 76) of 25% with a minimum arrestance of 90%.

- The media support shall be a welded wire grid with an effective open area of not less than 90%.  The grid shall be bonded to the filter media to eliminate media oscillation and pull away.

- The enclosing frame shall be constructed of rigid, heavy duty, high wet strength beverage board.  The frame shall be bonded to the filter pack.  Standard sizes shall be 12" x 24" x 2" and 24" x 24" x 2".

- Filters shall be Cam-Farr 30/30 or equal by American Air Filter, Eco-Air or Airguard.