The purpose of this standard is to establish consistency in the naming of components in the electrical distribution system and mechanical systems. It is intended to provide easy identification of a component's location, power supply, and load information from the equipment label solely and to make it easy to trace equipment power sources and loads for maintenance purposes. The following guidelines should apply in almost all cases for all electric powered equipment and electrical gear. For those items which cannot be produced from these guidelines, then further guidance should be obtained from the appropriate electrical systems supervisor.

Any label that belongs to equipment within the emergency power subsystem shall be RED with white lettering. All other labels shall be BLACK with white lettering. Additionally, all labels will have at least two lines—one designating the component name and the other designating the component’s power source. In the case of a component with multiple feeds, there shall be separate line for each power source component name.

Format:

The components will be labeled using the following format:

ID: Room No./Equipment name-Specific device number

Fed from: Room No./Equipment name-Specific device number

Each field has a specified number of characters and is defined as follows:

Room (up to 5 capitalized characters) => the room in which the component is located; if component is in a corridor use "CORR".

Equipment Name (up to 8 capitalized characters) => the name of the particular type of equipment from the PPDMC equipment naming convention list shown below.

Specific Number (up to 3 characters) => the number of that particular device from the drawing or the next sequential number in that equipment type.

| Equipment Description | Equipment Name |
| --- | --- |
| Air Conditioning Units | ACU-x |
| Air Handler Units | AHU-x |
| Backflow Preventor | BFP-x |
| Chilled Water Pump | CHW/PMP-x |
| Chillers | CHL-x |
| Compactor | CPT-x |
| Condensate Pump | CND/PMP-x |
| Control Air Compressor | CA/CMP-x |
| Conveyor | CNV-x |
| Critical Branch Automatic Transfer Switch | C/ATS-x |
| Critical Branch Distribution Panel | C/DP-x |
| Critical Branch Motor Control Ctr | C/MCC-x |
| Critical Branch Panel | C/P-x |
| Critical Branch Switchboard | C/SWBD-x |
| Critical Branch Switchgear | C/SWGR-x |
| Critical Branch Transformer | C/T-x |
| Domestic Cold Water Pump | DCW/PMP-x |
| Domestic Hot Water Pump | DHW/PMP-x |
| Dumb Waiters | DUM-x |
| Elevators | ELEV-x |
| Emergency Automatic Transfer Switch | E/ATS-x |
| Emergency Distribution Panel | E/DP-x |
| Emergency Generator | EG-x |
| Emergency Motor Control Ctr | E/MCC-x |
| Emergency Panel | E/P-x |
| Emergency Switchboard | E/SWBD-x |
| Emergency Switchgear | E/SWGR-x |
| Emergency Transformer | E/T-x |
| Exhaust Fans | EXF-x |
| Fan Coil Unit | FCU-x |
| Fire Pump | SPR/PMP-x |
| Heat Exchanger | HTX-x |
| Hot Water Heater | HWH-x |
| Laboratory Air Compressor | LA/CMP-x |
| Laboratory Vacuum Pump | LV/PMP-x |
| Life Safety Automatic Transfer Switch | LS/ATS-x |
| Life Safety Distribution Panel | LS/DP-x |
| Life Safety Panel | LS/P-x |
| Life Safety Switchboard | LS/SWBD-x |
| Life Safety Switchgear | LS/SWGR-x |
| Life Safety Transformer | LS/T-x |
| Medical Air Compressor | AIR/CMP-x |
| Medical Vacuum Pump | VAC/PMP-x |
| Normal Power Automatic Transfer Switch | N/ATS-x |
| Normal Power Distribution Panel | N/DP-x |
| Normal Power Motor Control Ctr | N/MCC-x |
| Normal Power Panel | N/P-x |
| Normal Power Switchboard | N/SWBD-x |
| Normal Power Switchgear | N/SWGR-x |
| Normal Power Transformer | N/T-x |
| Reheat Pump | RHT/PMP-x |
| Tube System Transfer Station | TUBE/STN-x |
| Variable Speed Drive | VSD-x |

Examples:

A typical normal power distribution panel on the second floor of the main hospital in room H-201 might be labeled H201/N/DP-1.

A motor control center in the penthouse of the Combs building might be labeled 401/N/MCC-1.

A chilled water pump in H-46 might be labeled as H46/CHW/PMP-1 for the load designation and H46/N/P-3 for the source designation.

NOTE: The component identification number, or sequence number, is just a simple numbering of similar equipment on the same floor numbered from left to right as seen on the electrical distribution riser diagram provided by the architects. Therefore, it is important to note the building and floor when referring to a component to determine its location. If the components to be labeled are existing equipment or new equipment in an existing building, the component sequence number should be obtained from the appropriate electrical systems supervisor. If the equipment is being installed as part of a new building construction project, then the contractor may determine the sequence numbers.