- General

This standard applies to all glycol systems installed in PPDMC maintained buildings for energy recovery and/or HVAC systems.

2.0	Glycol concentration

Glycol systems are to be designed for using a 50% propylene glycol and 50% water mixture.  The systems are to be designed so the required heat transfer can be achieved with the 50/50 mixture.

3.0	Make-up System

Every glycol system must have a make-up system for the addition of the glycol/water mixture to the overall system.  The make-up system needs to have a mixing tank for mixing the glycol and water to maintain the 50/50 mixture in the system.  The mixing tank is to have a fill pump for pumping the mixture into the overall system.  The make – up water connection to the system is not to directly connect to the overall system in such a manner that non-mixed water could be introduced into the system.